## Sheet1
Calculate capillary size: |  |  |  |  | Based on Secop Database 2.2 from Secop Capillary Tube Selector software
Wattage (Kw): |  |  | 1 |  | Condensing temperature: 50°C, Return gas temperature: 32°C
Evaporating temperature |  |  | -30 |  | Results contain extrapolated data based on math formula constants derived from available data.
|  | Capillary size: | [16 empty] | Custom: | Flow rate (L/min):
Results (mm): |  | 0.6 | 0.63 | 0.7 | 0.71 | 0.8 | 0.9 | 1 | 1.12 | 1.2 | 1.25 | 1.4 | 1.5 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | 1.0101
R600A: |  | 9.4473 | 12.0861 | 20.4335 | 21.928 | 39.7661 | 71.6849 | 121.4461 | 214.024 | 302.2 | 370.6985 | 654.5295 | 926.5692 | 1284.2545 | 2339.0412 | 4016.9323 | 6574.8747 | 12792.006 | 127.7065 | 78.59
R134A |  | 8.3151 | 10.6024 | 17.9862 | 19.3119 | 35.0815 | 63.1619 | 106.9371 | 188.5008 | 266.1035 | 326.2138 | 572.918 | 805.4383 | 1105.5738 | 1959.8598 | 3248.9007 | 5102.8969 | 9269.3138 | 112.4494 | 83.53
1234YF |  | 3.7355 | 5.734 | 9.7057 | 10.4174 | 18.9282 | 34.1668 | 57.8789 | 101.9381 | 143.9661 | 176.7054 | 313.4288 | 446.1154 | 622.7947 | 1155.5699 | 2028.9282 | 3400.4006 | 6853.5969 | 60.8592 | 124.29
R513A |  | 15.2169 | 19.348 | 32.7289 | 35.1377 | 63.8595 | 115.0783 | 194.8758 | 343.4843 | 484.9971 | 594.7712 | 1047.1567 | 1476.3944 | 2034.3621 | 3643.5675 | 6119.5464 | 9758.7636 | 18184.8706 | 204.9199 | 61.94
R290 |  | 50.5173 | 69.4684 | 117.6865 | 126.3408 | 229.4827 | 413.5049 | 700.2414 | 1234.0843 | 1742.4768 | 2137.0202 | 3765.6589 | 5315.7516 | 7337.8619 | 13210.6714 | 22344.0913 | 35931.4509 | 67915.659 | 736.3281 | 33.8929
R22 |  | 29.5664 | 41.4468 | 70.1635 | 75.3165 | 136.7618 | 246.4709 | 417.4332 | 735.6628 | 1038.7108 | 1273.9341 | 2245.6189 | 3171.7296 | 4381.7861 | 7907.2529 | 13416.2784 | 21655.1476 | 41186.7369 | 438.9473 | 44.33
R407C |  | 23.497 | 30.007 | 50.8762 | 54.6197 | 99.2005 | 178.7001 | 302.5995 | 533.3005 | 752.9 | 923.2031 | 1624.8602 | 2290.6457 | 3156.4342 | 5656.4156 | 9512.0814 | 15196.8354 | 28421.723 | 318.1948 | 49.66
R404A |  | 14.0849 | 18.0163 | 30.5517 | 32.7976 | 59.549 | 107.2827 | 181.6764 | 320.1875 | 452.0983 | 554.4777 | 977.2408 | 1379.9033 | 1905.6335 | 3435.2169 | 5820.6512 | 9380.6242 | 17797.3244 | 191.0395 | 43.003
R507 |  | 9.6416 | 11.9972 | 20.3291 | 21.833 | 39.7398 | 71.5815 | 121.1671 | 213.5523 | 301.4507 | 369.514 | 648.4314 | 910.4763 | 1247.3918 | 2198.3618 | 3613.4249 | 5614.0235 | 9994.1955 | 127.4103 | 77.7852
Info & Disclaimer:
www.hydrocarbonconspiracy.info
Facebook: "Hydrocarbon Conspiracy"
Please check the main PDF document and other resources!
My technical research is based on much analysis of publicly available data, but isn’t endorsed by any of the hydrocarbon gas manufacturers.
Not endorsed by the hydrocarbon refrigerant manufacturers.
Not endorsed by Secop.
More refrigerants will be added in, once the correlation between the refrigerant and the capillary size / flow rate is established. This tool is intended to help generate custom capillary tubes for the given refrigerants.
Figures based on evaporating temperature -40, condensing temperature 50, return gas temperature 32
Watts | Refrigerant | 0.6 | 0.63 | 0.7 | 0.71 | 0.8 | 0.9 | 1 | 1.12 | 1.2 | 1.25 | 1.4 | 1.5 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | Flow rate L/m
200 | R600A |  | 290 | 490 | 520 | 950 | 1700 | 2890 | 5090 | 7180 | 8810 | [7 empty] | 16.1
200 | R134A | Invalid range, -35°C - 15°C required
200 | R1234YF | Invalid range, -35°C - 15°C required
200 | R513A | Invalid range, -35°C - 15°C required
200 | R290 | 1170 | 1490 | 2520 | 2700 | 4910 | 8850 | 14990 | 26410 | 37290 | [8 empty] | 7.1
200 | R22 | 660 | 840 | 1420 | 1530 | 2770 | 4990 | 8460 | 14900 | 21040 | [8 empty] | 9.4
200 | R407C | Invalid range, -15°C - 10°C required
200 | R404A | 530 | 680 | 1150 | 1240 | 2250 | 4050 | 6860 | 12090 | 17080 | [8 empty] | 10.5
200 | R507 |  | 290 | 490 | 530 | 960 | 1730 | 2930 | 5160 | 7290 | 8940 | [7 empty] | 16
Figures based on evaporating temperature -40, condensing temperature 50, return gas temperature 32
Watts | Refrigerant | 0.6 | 0.63 | 0.7 | 0.71 | 0.8 | 0.9 | 1 | 1.12 | 1.2 | 1.25 | 1.4 | 1.5 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | Flow rate L/m
400 | R600A |  |  |  |  | 240 | 430 | 720 | 1270 | 1800 | 2200 | 3880 | 5480 | 7570 |  |  |  |  | 32.2
400 | R134A | Invalid range, -35°C - 15°C required
400 | R1234YF | Invalid range, -35°C - 15°C required
400 | R513A | Invalid range, -35°C - 15°C required
400 | R290 |  | 370 | 630 | 680 | 1230 | 2210 | 3750 | 6610 | 9330 | 11450 | [7 empty] | 14.1
400 | R22 |  |  | 360 | 380 | 690 | 1250 | 2120 | 3730 | 5270 | 6460 | 11380 | [6 empty] | 18.8
400 | R407C | Invalid range, -15°C - 10°C required
400 | R404A |  |  | 370 | 390 | 720 | 1290 | 2180 | 3850 | 5440 | 6670 | 11750 | [6 empty] | 18.5
400 | R507 |  |  |  |  | 240 | 430 | 730 | 1290 | 1830 | 2240 | 3950 | 5570 | 7690 |  |  |  |  | 32
Figures based on evaporating temperature -40, condensing temperature 50, return gas temperature 32
Watts | Refrigerant | 0.6 | 0.63 | 0.7 | 0.71 | 0.8 | 0.9 | 1 | 1.12 | 1.2 | 1.25 | 1.4 | 1.5 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | Flow rate L/m
500 | R600A | [5 empty] | 270 | 460 | 810 | 1150 | 1410 | 2480 | 3510 | 4840 | 8730 |  |  |  | 40.3
500 | R134A | Invalid range, -35°C - 15°C required
500 | R1234YF | Invalid range, -35°C - 15°C required
500 | R513A | Invalid range, -35°C - 15°C required
500 | R290 |  | 240 | 400 | 430 | 790 | 1420 | 2400 | 4230 | 5970 | 7330 | [7 empty] | 17.7
500 | R22 |  |  | 230 | 240 | 440 | 800 | 1360 | 2390 | 3370 | 4140 | 7290 | [6 empty] | 23.5
500 | R407C | Invalid range, -15°C - 10°C required
500 | R404A |  |  | 250 | 270 | 480 | 870 | 1470 | 2600 | 3660 | 4490 | 7920 | [6 empty] | 22.6
500 | R507 | [5 empty] | 280 | 470 | 830 | 1170 | 1430 | 2530 | 3570 | 4920 | 8870 |  |  |  | 40
Figures based on evaporating temperature -40, condensing temperature 50, return gas temperature 32
Watts | Refrigerant | 0.6 | 0.63 | 0.7 | 0.71 | 0.8 | 0.9 | 1 | 1.12 | 1.2 | 1.25 | 1.4 | 1.5 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | Flow rate L/m
1000 | R600A | [8 empty] | 290 | 350 | 620 | 880 | 1210 | 2180 | 3690 | 5950 | 11270 | 80.6
1000 | R134A | Invalid range, -35°C - 15°C required
1000 | R1234YF | Invalid range, -35°C - 15°C required
1000 | R513A | Invalid range, -35°C - 15°C required
1000 | R290 | [5 empty] | 350 | 600 | 1060 | 1490 | 1830 | 3230 | 4560 | 6300 | 11350 |  |  |  | 35.3
1000 | R22 | [6 empty] | 340 | 600 | 840 | 1030 | 1820 | 2570 | 3550 | 6400 | 10850 |  |  | 47
1000 | R407C | Invalid range, -15°C - 10°C required
1000 | R404A | [6 empty] | 410 | 720 | 1020 | 1250 | 2210 | 3120 | 4300 | 7750 | 13130 |  |  | 42.8
1000 | R507 | [8 empty] | 290 | 360 | 630 | 890 | 1230 | 2220 | 3760 | 6050 | 11470 | 79.9
Flow rates (L/min) @ 10Kw: |  |  |  | R600A | R134A | 1234YF | R513A | R290 | R22 | R407C | R404A | R507
Evaporating temperature -15°C |  |  |  | 752.4 | 780.1 | 1171.4 | 665.8 | 324.5 | 417.8 | 496.6 | 434.6 | 759.9
Evaporating temperature -25°C |  |  |  | 775.2 | 815.9 | 1216.2 | 631.7 | 333.2 | 432.8 | Invalid | 442.5 | 770
Evaporating temperature -30°C |  |  |  | 785.9 | 835.3 | 1242.9 | 619.4 | 338.9 | 443.3 | Invalid | 436.8 | 777.9
Evaporating temperature -40°C |  |  |  | 806 | Invalid | Invalid | Invalid | 353.3 | 470.3 | Invalid | 406.2 | 798.9
Extrapolated formulas:
Enter:
Evaporating temperature
Wattage
Flow rate: | [12 empty] | Flow rate:
Enter evaporating temperature: |  |  |  | -15 | [8 empty] | Polynomial, quadratic regression, 2nd order polynomial
Enter wattage (Kw): |  |  |  | 10 | [8 empty] | R600A: | y = 714.8442 - 2.638846*x - 0.009*x^2
Refrigerant: |  |  | R600A | R134A | R1234YF | R290 | R22 | R407C | R404A | R507 |  |  | R134A | y = 733.9 - 2.78*x + 0.02*x^2
Flow rate (L/min): |  |  | 752.4 | 780.1 | 1171.4 | 324.5058 | 417.8 |  | 430.025 | 759.8903 |  |  | 1234YF | y = 1125.7 - 2.186667*x + 0.05733333*x^2
[13 empty] | R513A | y = 740.7 + 5.943333*x + 0.06333333*x^2
Flow rate % difference from base -15°C: | [12 empty] | R290 | y = 318.6327 - 0.1065385*x + 0.019*x^2
[13 empty] | R22 | y = 410.3 + 0.1*x + 0.04*x^2
[13 empty] | R407C | 496.6
R404A
Polynomial, quintic regression, 5th order polynomial
Capillary sizing (Based on 100W @ -15°C):
[13 empty] | R600A: | y = -6299.89 + 36440.61*x - 82768.52*x^2 + 92376.69*x^3 - 50731.16*x^4 + 24232.03*x^5
[13 empty] | R134A | y = 6133.931 - 36911.32*x + 87287.3*x^2 - 101415.9*x^3 + 57934.83*x^4 - 775.8807*x^5
[13 empty] | 1234YF | y = -5149.379 + 30915.5*x - 73073.59*x^2 + 84950.94*x^3 - 48575.76*x^4 + 16371.76*x^5
[13 empty] | R513A | y = 5027.188 - 28469.49*x + 63587.57*x^2 - 70043.22*x^3 + 38058.48*x^4 + 8751.674*x^5
[13 empty] | R290 | y = 2850.441 - 16828.21*x + 38813.38*x^2 - 43759.71*x^3 + 24148.87*x^4 + 65652.12*x^5
[13 empty] | R22 | y = -2702.317 + 15731.84*x - 35865.55*x^2 + 40071.94*x^3 - 21978.72*x^4 + 47510.33*x^5
[13 empty] | R407C | y = 4326.217 - 26822.06*x + 65092.01*x^2 - 77381.15*x^3 + 45139.41*x^4 + 19905.52*x^5
[13 empty] | R404A | y = -1164.307 + 5799.282*x - 11329.14*x^2 + 10903.18*x^3 - 5196.634*x^4 + 21755.22*x^5
[13 empty] | R507 | y = 11429.35 - 66071.18*x + 150430.1*x^2 - 168765.8*x^3 + 93395.45*x^4 - 7487.241*x^5
Nonlinear, Power curve
Capillary sizing related to Wattage, based on -15°C evaporating temperature and 1.2mm capillary:
[13 empty] | R600A: | y = 332333400*x^-2.001721 | [6 empty] | 328.4059
[13 empty] | R134A | y = 279984400*x^-1.98156 | [6 empty] | 318.0196
[13 empty] | 1234YF | y = 133576300*x^-1.997213 | [6 empty] | 136.1728
[13 empty] | R513A | y = 421713800*x^-2.000419 | [6 empty] | 420.495
[13 empty] | R290 | y = 1738450000*x^-1.996867 | [6 empty] | 1776.4836
[13 empty] | R22 | y = 1049419000*x^-1.99696 | [6 empty] | 1071.6894
[13 empty] | R407C | y = 487632700*x^-1.906152 | [6 empty] | 932.4742
[13 empty] | R404A | y = 87480040*x^-1.613877 | [6 empty] | 1259.7315
[13 empty] | R507 | y = 317370900*x^-1.997057 | [6 empty] | 323.8889
Polynomial, quadratic regression, 2nd order polynomial
Percentage offset of capillary sizing based on 1.2mm capillary, 100W, and base evaporator temperature of -15°C:
Where -15°C = 100% and lower numbers are less.
[13 empty] | R600A: | y = 110.215 + 0.743372*x + 0.004145182*x^2 | [6 empty] | 91.6445
[13 empty] | R134A | y = 113.4142 + 0.9172406*x + 0.001530556*x^2 | [6 empty] | 87.2745
[13 empty] | 1234YF | y = 109.3865 + 0.566642*x - 0.003941858*x^2 | [6 empty] | 88.8396
[13 empty] | R513A | y = 78.16584 - 1.664687*x - 0.01393839*x^2 | [6 empty] | 115.5619
[13 empty] | R290 | y = 105.0656 + 0.2289621*x - 0.007219671*x^2 | [6 empty] | 91.699
[13 empty] | R22 | y = 106.5418 + 0.2815766*x - 0.01024244*x^2 | [6 empty] | 88.8763
R407C
[13 empty] | R404A | y = 129.8762 + 2.570304*x + 0.03857069*x^2 | [6 empty] | 87.4807
[13 empty] | R507 | y = 100.9427 - 0.05694906*x - 0.007978448*x^2 | [6 empty] | 95.4706
Wattage multiplier:
Where 100W = 100%, 1Kw = 1%
[13 empty] | Enter wattage (Kw): |  |  | 0.1
[13 empty] | Result: |  |  | 100